## Slide 1: Low Flow Chemical Dose Controller
Kaylyn Bacha
Danielle Feng Kwabena Nimo

## Slide 2: Purpose
The LCDC doses PACl to water for flocculation as it enters the plant and chlorine to water in the exit tank

## Slide 3: Plant Setup
Picture/Graph/Table

## Slide 4: Design Theory
The Hagen-Poiseuille Equation assumes flow is laminar, viscous, and incompressible
The LCDC is designed so that major losses outweigh minor losses, maintaining a linear relationship between flow rate and total head loss.

## Slide 5: Summer 2013 Challenges
Design low flow doser using half size 20” dosing arm
Test 1/16’’ dosing tubes with PACl
Design adjustable system for constant head tanks
Ensure system is chlorine resistant

## Slide 6: Experimental Setup
Text
Picture/Graph/Table
Constant Head Tank
Dosing Tubes
Lever Arm
Drop Tube
PACl stock tank

## Slide 7: Procedures
Calibrate the lever arm
Measure the flow rate of water from drop tube
Check 1/16” tubing for clogging periodically

## Slide 8: Troubleshooting
Calibrate system before every use
Make sure the water level in the CHT is constant over time
No kinks in tubes
No air bubbles

## Slide 9: Water Trials
Chart: Water Flow Through LCDC
| 0 | 10 | 15 | 20
1/16 tubes, short lever | 0 | 0.37669 | 0.69811 | 0.96188
1/16 tubes, long lever | 0 | 0.61503 | 0.91633 | 1.2365
1/8 tubes, short lever | 0 | 2.4954 | 5.3856 | 7.5155 | 9.4863
1/8 tubes, long lever | 0 | 2.2318 | 4.8098 | 6.8105 | 8.0106
Difference in flow rate with wider tubes when comparing performance of lever arms

## Slide 10: Water Trial Data
 | Large Lever Arm |  | Small Lever Arm | 
Average flow rate | 1/8” tubing 1.3 m | 1/16” tubing 1 m | 1/8” tubing 1.3 m | 1/16” tubing 1 m
20cm | 8.01 | 0.94 | 9.49 | 0.75
15cm | 6.81 | 0.65 | 7.52 | 0.57
10cm | 4.81 | 0.43 | 5.39 | 0.35
5cm | 2.23 |  | 2.49 | 
In general, half size small lever arm decreases flow rate
Dosing tube diameter most dramatic reduction of flow rate

## Slide 11: PACl Trials
Chart: 40mg/L PACl Coagulant Dose
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
20cm | 0.80671 | 0.81116 | 0.80645 | 0.80154 | 0.80802 | 0.85179 | 0.78272 | 0.78839 | 0.8109 | 0.78542 | 0.86931 | 0.84293 | 0.85034 | 0.82622 | 0.84293 | 0.84938 | 0.83033 | 0.82418 | 0.83752 | 0.81301 | 0.86806 | 0.88339 | 0.89286 | 0.87108 | 0.9058 | 0.89286 | 0.90253 | 0.9058 | 0.89286 | 0.89928
15cm | 0.5997 | 0.61728 | 0.5891 | 0.57937 | 0.59701 | 0.60259 | 0.58893 | 0.61576 | 0.59934 | 0.59154 | 0.6006 | 0.59737 | 0.60168 | 0.58743 | 0.59418 | 0.5969 | 0.58789 | 0.58434 | 0.59952 | 0.5864 | 0.68681 | 0.66138 | 0.68871 | 0.68306 | 0.69444 | 0.67935 | 0.68306 | 0.67751 | 0.66845 | 0.69252
10cm | 0.36617 | 0.38023 | 0.37843 | 0.3803 | 0.36996 | 0.36826 | 0.36711 | 0.37821 | 0.37355 | 0.37369 | 0.42833 | 0.43128 | 0.42409 | 0.47348 | 0.45208 | 0.45208 | 0.46642 | 0.45455 | 0.46125 | 0.46296 | 0.46041 | 0.4529 | 0.45872
Difficult to get steady flow rates
Flow rate changes when flow is stopped, then started again
No clogging issues
Air bubbles in tubes become bigger issue

## Slide 12: Tube Connectors Chlorine Test
After
Before
No visible degradation of plastic in 30% chlorine solution after 48 hours
Connector between manifold and dosing tubes

## Slide 13: New Adjustable Head Tank
Looking into a sliding bar device, found a couple of options
Turn buckle requires disconnecting tubes from CHT
New device would allow for linear adjustment of head tank height, instead of step-wise adjustment with chain
More precision, and allows for easy measurement of head tank height

## Slide 14: Future Work
Run more trials for PACl, adjusting for consistency
Test out adjustable head tank slider
Automated flow rate measurement system (flow meter device?)
Design more permanently built setup to reduce variability between teams of different semesters
Standardize all tube lengths

## Slide 15: Questions?